## KPI Summary
ASSET INVESTMENT PLANNING — KPI SUMMARY & SCENARIO RATINGS
IEEE 30-Bus · 4 Scenarios · 14 KPIs · Verified: AO1=Very Good ¦ S1=Bad ¦ S2=Good ¦ S3=Excellent
AO1 ▶ VERY GOOD |  |  |  | S1 ▶ BAD |  |  |  | S2 ▶ GOOD |  |  |  | S3 ▶ EXCELLENT
14/14 compliance · 12/14 strategic |  |  |  | 12/14 compliance · 0/14 strategic |  |  |  | 14/14 compliance · 1/14 strategic |  |  |  | 14/14 compliance · 14/14 strategic
IEEE 30-Bus base case — Gen Bus13 (85MW) + Bus22 (60MW) |  |  |  | Bus31 (500MW) via Bus28+Bus29 — no local generation |  |  |  | Bus31 (500MW) via Bus27+Bus29 — new Gen Bus32 (200MW) |  |  |  | Bus31 (500MW) via Bus28+Bus30 — Gen Bus32 (400MW) + Gen Bus33 (300MW)
KPI DETAIL — COMPLIANCE & STRATEGIC RESULTS
Analysis | KPI Metric | Comp. Limit | Strat. Limit | AO1 | C | S | S1 | C | S | S2 | C | S | S3 | C | S
Load Flow | Max Branch Loading (%) | <=100 | <=75 | 74.8 | PASS | PASS | 98.8 | PASS | GAP | 88.4 | PASS | GAP | 62.4 | PASS | PASS
Load Flow | Min Bus Voltage (pu) | >=0.95 | >=0.97 | 1.003 | PASS | PASS | 0.962 | PASS | GAP | 0.952 | PASS | GAP | 1.008 | PASS | PASS
Load Flow | Total P Loss (MW) | <=40 | <=15 | 12.4 | PASS | PASS | 38.4 | PASS | GAP | 26.4 | PASS | GAP | 8.8 | PASS | PASS
Contingency | Max Post-Cont Loading (%) | <=125 | <=90 | 91.4 | PASS | GAP | 124.8 | PASS | GAP | 122.3 | PASS | GAP | 86.4 | PASS | PASS
Contingency | N-1 Contingency Violations | <=2 | <=0 | 0 | PASS | PASS | 2 | PASS | GAP | 1 | PASS | GAP | 0 | PASS | PASS
Contingency | Min Post-Cont Voltage (pu) | >=0.9 | >=0.93 | 0.938 | PASS | PASS | 0.904 | PASS | GAP | 0.908 | PASS | GAP | 0.951 | PASS | PASS
Short Circuit | Max Fault Current (kA) | <=17 | <=14 | 14.82 | PASS | GAP | 16.84 | PASS | GAP | 15.44 | PASS | GAP | 13.44 | PASS | PASS
Short Circuit | Max Breaker Duty (%) | <=85 | <=65 | 63.4 | PASS | PASS | 84.8 | PASS | GAP | 81.3 | PASS | GAP | 64.8 | PASS | PASS
Transient | Max Rotor Angle (deg) | <=40 | <=25 | 23.4 | PASS | PASS | 36.8 | PASS | GAP | 30.44 | PASS | GAP | 18.88 | PASS | PASS
Transient | Post-Fault V Recovery (pu) | >=0.88 | >=0.92 | 0.924 | PASS | PASS | 0.868 | FAIL | GAP | 0.906 | PASS | GAP | 0.951 | PASS | PASS
Transient | Max Freq Deviation (Hz) | <=0.5 | <=0.3 | 0.216 | PASS | PASS | 0.421 | PASS | GAP | 0.306 | PASS | GAP | 0.152 | PASS | PASS
VAR/Harmonics | Min Post-Comp Voltage (pu) | >=0.92 | >=0.97 | 1.022 | PASS | PASS | 0.888 | FAIL | GAP | 0.954 | PASS | GAP | 0.988 | PASS | PASS
VAR/Harmonics | Max Harmonic TDD (%) | <=12 | <=5 | 4.8 | PASS | PASS | 11.8 | PASS | GAP | 7.8 | PASS | GAP | 4.8 | PASS | PASS
VAR/Harmonics | IEEE 519 Violations | <=2 | <=0 | 0 | PASS | PASS | 2 | PASS | GAP | 0 | PASS | PASS | 0 | PASS | PASS

## KPI Detail
KPI DETAIL — All 14 KPIs × 4 Scenarios
Green=Pass/Meet · Red=Compliance Fail · Yellow=Strategic Gap · Threshold Direction shown
Analysis | KPI Metric | Comp. | Strategic | AO1 Value | C | S | S1 Value | C | S | S2 Value | C | S | S3 Value | C | S
Load Flow | Max Branch Loading (%) | <=100 | <=75 | 74.8 | ✓ | ✓ | 98.8 | ✓ | ~ | 88.4 | ✓ | ~ | 62.4 | ✓ | ✓
Load Flow | Min Bus Voltage (pu) | >=0.95 | >=0.97 | 1.003 | ✓ | ✓ | 0.962 | ✓ | ~ | 0.952 | ✓ | ~ | 1.008 | ✓ | ✓
Load Flow | Total P Loss (MW) | <=40 | <=15 | 12.4 | ✓ | ✓ | 38.4 | ✓ | ~ | 26.4 | ✓ | ~ | 8.8 | ✓ | ✓
Contingency | Max Post-Cont Loading (%) | <=125 | <=90 | 91.4 | ✓ | ~ | 124.8 | ✓ | ~ | 122.3 | ✓ | ~ | 86.4 | ✓ | ✓
Contingency | N-1 Contingency Violations | <=2 | <=0 | 0 | ✓ | ✓ | 2 | ✓ | ~ | 1 | ✓ | ~ | 0 | ✓ | ✓
Contingency | Min Post-Cont Voltage (pu) | >=0.9 | >=0.93 | 0.938 | ✓ | ✓ | 0.904 | ✓ | ~ | 0.908 | ✓ | ~ | 0.951 | ✓ | ✓
Short Circuit | Max Fault Current (kA) | <=17 | <=14 | 14.82 | ✓ | ~ | 16.84 | ✓ | ~ | 15.44 | ✓ | ~ | 13.44 | ✓ | ✓
Short Circuit | Max Breaker Duty (%) | <=85 | <=65 | 63.4 | ✓ | ✓ | 84.8 | ✓ | ~ | 81.3 | ✓ | ~ | 64.8 | ✓ | ✓
Transient | Max Rotor Angle (deg) | <=40 | <=25 | 23.4 | ✓ | ✓ | 36.8 | ✓ | ~ | 30.44 | ✓ | ~ | 18.88 | ✓ | ✓
Transient | Post-Fault V Recovery (pu) | >=0.88 | >=0.92 | 0.924 | ✓ | ✓ | 0.868 | ✗ | ~ | 0.906 | ✓ | ~ | 0.951 | ✓ | ✓
Transient | Max Freq Deviation (Hz) | <=0.5 | <=0.3 | 0.216 | ✓ | ✓ | 0.421 | ✓ | ~ | 0.306 | ✓ | ~ | 0.152 | ✓ | ✓
VAR/Harmonics | Min Post-Comp Voltage (pu) | >=0.92 | >=0.97 | 1.022 | ✓ | ✓ | 0.888 | ✗ | ~ | 0.954 | ✓ | ~ | 0.988 | ✓ | ✓
VAR/Harmonics | Max Harmonic TDD (%) | <=12 | <=5 | 4.8 | ✓ | ✓ | 11.8 | ✓ | ~ | 7.8 | ✓ | ~ | 4.8 | ✓ | ✓
VAR/Harmonics | IEEE 519 Violations | <=2 | <=0 | 0 | ✓ | ✓ | 2 | ✓ | ~ | 0 | ✓ | ✓ | 0 | ✓ | ✓

## Scenario Comparison
SCENARIO COMPARISON — Engineering Summary
Scenario | Rating | Bus31 Connection | Added Generators | Comp. KPIs Pass | Strat. KPIs Pass | P-Loss (MW) | Max Loading % | Min Bus V (pu) | Recommendation
AO1 | Very Good | Bus28+Bus29 Base | Bus13 85MW, Bus22 60MW | 14/14 | 12/14 | 12.4 | 74.8 | 1.003 | Monitor — minor strategic gaps
S1 | Bad | Bus28+Bus29 | None | 12/14 | 0/14 | 38.4 | 98.8 | 0.962 | NOT APPROVED — 2 compliance failures
S2 | Good | Bus27+Bus29 | Bus32 200MW | 14/14 | 1/14 | 26.4 | 88.4 | 0.952 | Conditionally approved — upgrade Bus32 to 350MW+
S3 | Excellent | Bus28+Bus30 | Bus32 400MW + Bus33 300MW | 14/14 | 14/14 | 8.8 | 62.4 | 1.008 | RECOMMENDED — Excellent rating

## File Import Guide
PSS®E FILE IMPORT GUIDE — AIP Tool Testing
How to use the test files with the AIP Technical Evaluation Tool
STEP | ACTION | FILE TO USE | WHERE IN TOOL | EXPECTED RESULT
1 | Open AIP Tool | AIP_Tool_Final.html | Open in Chrome/Edge | Dashboard loads with 4 scenarios
2 | Import AO1 RAW topology | IEEE30_AO1.raw | Files > AO1 tab > Browse *.raw | SLD shows 30-bus network, voltages auto-loaded
3 | Import S3 RAW topology | IEEE30_S3.raw | Files > S3 tab > Browse *.raw | SLD shows 33-bus network (Bus31/32/33 added)
4 | Import AO1 load flow | AO1_loadflow.csv | Files > AO1 > Load Flow > Paste CSV | Load Flow tab updates with AO1 bus data
5 | Import S1 load flow | S1_loadflow.csv | Files > S1 > Load Flow > Paste CSV | Bus29/31 undervoltage highlighted in red
6 | Import S2 load flow | S2_loadflow.csv | Files > S2 > Load Flow > Paste CSV | Bus27/31 at compliance boundary
7 | Import S3 load flow | S3_loadflow.csv | Files > S3 > Load Flow > Paste CSV | All buses green, excellent voltages
8 | Import contingency files | AO1/S1/S2/S3_contingency.acc | Files > each scenario > Contingency | ACCC results populate, violations shown
9 | Import short circuit | AO1/S3_shortcircuit.dat | Files > Short Circuit | Fault currents and breaker duties populated
10 | Import transient | AO1/S3_transient.out | Files > Transient | Time-series data shows angle/voltage/freq
11 | View Network SLD | — | Network SLD View | Interactive diagram with voltage overlay
12 | Check KPI Dashboard | — | KPI Dashboard | Ratings: AO1=Very Good, S1=Bad, S2=Good, S3=Excellent
13 | Test Derogation | — | Derogation > S1 > toggle off Contingency | S1 score improves, derogated rating shown
14 | Add New Scenario | — | Scenarios > + Add Scenario | New scenario appears in all views/dropdowns
15 | Adjust Weights | — | Weightings | KPI scores update in real-time

## CSV Format Reference
CSV FORMAT REFERENCE — Paste Import Formats
LOAD FLOW
Headers | bus,name,type,v_pu,angle_deg,pgen_mw,qgen_mvar,pload_mw,qload_mvar,ploss_mw
Example | 1,BUS-1,SLACK,1.060,0.00,220.4,-12.1,0.0,0.0,1.8 2,BUS-2,PV,1.043,-4.82,40.0,42.3,21.7,12.7,0.4
CONTINGENCY
Headers | cont_id,label,type,element,post_flow_mva,post_loading_pct,rating_mva,viol_bus,pre_v_pu,post_v_pu,delta_v,status
Example | C001,L1-2,N-1,Line 1-2,91.4,73.1,125.0,Bus4,0.983,0.938,-0.045,OVERLOAD
SHORT CIRCUIT
Headers | bus,name,kv_base,i_fault_3ph_ka,i_fault_pu,xr_ratio,breaker_duty_pct,severity
Example | 1,BUS-1,132,13.84,7.36,14.8,63.4,OK
TRANSIENT
Headers | time_s,bus1_v_pu,bus6_v_pu,gen1_angle_deg,gen2_angle_deg,gen1_speed_pu,freq_hz
Example | 0.000,1.0000,0.9940,0.000,5.230,1.00000,60.000 1.017,0.8340,0.5580,10.88,16.14,0.99960,59.934